## Terms
Tj | °C | Some outdoor temperature | Dry-bulb (true thermodynamic T), not wet-bulb=f(dry,rH)=dry@100%rH
hj (bin hours) | h | Hours per season in which Tj occurs (Table G-1) | Ok
bin | N/A | Tj during hj (Table G-1) | Ok
Season | N/A | One of four sets of operating conditions (bins) | Ok
Pdc(Tj), Pdh(Tj), DC | kW | Declared (full compr.) capacity (cooling or heating) | Declared capacity of vapour compression of AC @ Tout=Tj & Tin without suppl. heaters
Pdesignc, Pdesignh | kW | Declared design (full compr.) load (cooling or heating) | Pdc(Tj) @ Tj=Tdesignc or Ph(Tj) @ Tj=Tdesignh
Tdesignc, Tdesignh | °C | Reference design T (cooling or heating) (Table G-3) | at which pl(Tj)=1. Cout: 35dry 24wet , Cin: 27 19 , H: avg, colder, warmer
Pc(Tj), Ph(Tj) | kW | Part-load (cooling or heating) | Load @ specific Tj = Pdesignc * pl(Tj) or Pdesignh * pl(Tj)
Bin limit T | °C | 16 | Limit in the bin for which no more cooling or heating in required
pl(Tj) | °C/°C=1 | Part-load ratio (cooling or heating) | (Tout-16)/(Tdesign-16)
Tbivalent | °C | Bivalent temperature | Lowest T at which 100% of heating load (Ph) is met without backup heater
TOL | °C | Operating limit temperature | Lowest T below which no heating capacity is declared (zero is declared)
HCE | h/a | Equivalent active mode hours for cooling (Table G-4) | Assumed annual hrs for Pdesignc to satisfy QC
HHE | h/a | Equivalent active mode hours for heating (Table G-4) | Assumed annual hrs for Pdesignh to satisfy QH
QC | kWh/a | Reference annual cooling demand | Pdesignc * HCE
QH | kWh/a | Reference annual heating demand (3 demands) | For a heating season =Pdesignh * HHE (equivalent)
EERd(Tj) | kW/kW=1 | Declared EER | Declared EER @ a limited no. of specified bins
COPd(Tj) | kW/kW=1 | Declared COP | Declared COP @ a limited no. of specified bins
EERd | kW/kW=1 | EER at declared capacity | Pdc(Tj) / effective power input at specific T's: A,B,C,D
COPd | kW/kW=1 | COP at declared capacity | Pdh(Tj) / effective power input at specific T's: A,B,C,D,E,F,G
EERbin(Tj) | kW/kW=1 | Bin-specific EER | EER specified for evry bin in a season, f(Pc(Tj),Pdc(Tj),EERd(Tj)) extra. 4 other bins
COPbin(Tj) | kW/kW=1 | Bin-specific COP | COP specified for evry bin in a season, f(Ph(Tj),Pdh(Tj),COPd(Tj)) extra. 4 other bins
EERbin | kW/kW=1 | EER at part-load | Cooling capacity at part-load or full/effective power input at specific T
COPbin | kW/kW=1 | COP at part-load | Heating capacity at part-load or full/effective power input at specific T
SEERon | kWh/kWh=1 | Active mode seasonal EER | Avg. cooling EER in active mode, f(Pc(Tj),EERbin(Tj)s), weighted by hj
SCOPon | kWh/kWh=1 | Active mode seasonal COP | Avg. COP in active mode for heating season, f(Ph(Tj),COPbin(Tj)s,PH), weighted by hj
QCE | kWh/a | Annual electricity consumption for cooling | Electricity consumption(C) to meet QC
QHE | kWh/a | Annual energy consumption for heating | Electricity consumption(C) to meet indicated (season) QH
SEER | kWh/kWh=1 | Seasonal EER | QC/QCE
SCOP | kWh/kWh=1 | Seasonal COP | QH/QHE
ηs | kW/kW=1 | Seasonal space heating efficiency | Season space heating demand of heater/annual energy consumption required
CR | kW/kW=1 | Capacity ratio | Cooling or heating part-load or full/ Pdc or Pdh at same T conds.
Cdc, Cdh | kW/kW=2 | Degradation co-officieint | Measure of efficiency loss in cooling or heating due to cycling of unit (measured or given)
Pcycc, Pcych | kWh | Cycling interval capacity for cooling or heating | time weighed average cooling capacity output over cycling interval test
EERcyc | kWh/kWh=1 | Cycling interval efficiency for cooling | Average EER over the cycling interval test=integrated cooling capacity/integrated Pin
COPcyc | kWh/kWh=1 | Cycling interval efficiency for heating | Average COP over the cycling interval test=integrated heating capacity/integrated Pin
Note on D27: Author: = QC/ SEERon+Cthermos-off+Cstandby+Coff+Ccrankcase heater during cooling season)
Note on D28: Author: = QH/ SCOPon+Cthermos-off+Cstandby+Coff+Ccrankcase heater during cooling season)

## Cooling Air-Air
A-D | DC | Pin | EERd | Pc | CR=Pc/DC | EERbin | Tj | hj | Pc(Tj) | EERbin(Tj) | 4769.4737 | 622.3596 | SEERon | HCE | QC | SEER
35 | 5 | 1.56 | 3.2051 | 5 | 1 | 3.2051 | 17 | 205 | 0.26316 | 12.2442 | 53.9474 | 4.406 | 7.6635 | 350 | 1750 | 6.5536
30 | 3.7 | 0.69 | 5.3623 | 3.6842 | 0.99573 | 5.3566 | 18 | 227 | 0.52632 | 12.2442 | 119.4737 | 9.7576 | HTO | PTO | QCE
25 | 2.4 | 0.25 | 9.6 | 2.3684 | 0.98684 | 9.5684 | 19 | 225 | 0.78947 | 12.2442 | 177.6316 | 14.5075 | 221 | 0.049 | 267.0292
20 | 2 | 0.144 | 13.8889 | 1.0526 | 0.52632 | 12.2442 | 20 | 225 | 1.0526 | 12.2442 | 236.8421 | 19.3433 | HSB | PSB
[5 empty] | Cdc |  | 21 | 216 | 1.3158 | 11.709 | 284.2105 | 24.2728 | 2142 | 0.013
[5 empty] | 0.25 |  | 22 | 215 | 1.5789 | 11.1739 | 339.4737 | 30.3811 | HCK | PCK
[7 empty] | 23 | 218 | 1.8421 | 10.6387 | 401.5789 | 37.7469 | 2672 | 0
[7 empty] | 24 | 197 | 2.1053 | 10.1036 | 414.7368 | 41.0486 | HOFF | POFF
[7 empty] | 25 | 178 | 2.3684 | 9.5684 | 421.5789 | 44.0594 | 0 | 0
[7 empty] | 26 | 158 | 2.6316 | 8.7261 | 415.7895 | 47.6492
[7 empty] | 27 | 137 | 2.8947 | 7.8837 | 396.5789 | 50.3037
[7 empty] | 28 | 109 | 3.1579 | 7.0413 | 344.2105 | 48.8843
[7 empty] | 29 | 88 | 3.4211 | 6.199 | 301.0526 | 48.565
[7 empty] | 30 | 63 | 3.6842 | 5.3566 | 232.1053 | 43.3307
[7 empty] | 31 | 39 | 3.9474 | 4.9263 | 153.9474 | 31.2501
[7 empty] | 32 | 31 | 4.2105 | 4.496 | 130.5263 | 29.0316
[7 empty] | 33 | 24 | 4.4737 | 4.0657 | 107.3684 | 26.4082
[7 empty] | 34 | 17 | 4.7368 | 3.6354 | 80.5263 | 22.1505
[7 empty] | 35 | 13 | 5 | 3.2051 | 65 | 20.28
[7 empty] | 36 | 9 | 5.2632 | 3.2051 | 47.3684 | 14.7789
[7 empty] | 37 | 4 | 5.5263 | 3.2051 | 22.1053 | 6.8968
[7 empty] | 38 | 3 | 5.7895 | 3.2051 | 17.3684 | 5.4189
[7 empty] | 39 | 1 | 6.0526 | 3.2051 | 6.0526 | 1.8884
[7 empty] | 40 | 0 | 6.3158 | 3.2051 | 0 | 0
Note on A1: Author: Part-load T conditions (Table-2 pg23 14825-2016)
Note on B1: Author: At rated conditions
Note on C1: Author: Effective power input at rated conditions: compressor, defrosting, control & safety device, fans, pumps
Note on D1: Author: =DC/Pin
Note on E1: Author: =Pdesignc*pl If Tdesignc=35 (reference design condition for cooling) Pdesignc=DC @ 35
Note on H1: Author: Tj,hj (Table-A1 pg55 14825-2016)
Note on I1: Author: Tj,hj (Table-A1 pg55 14825-2016)
Note on K1: Author: EERbin above A, EERbinA is used EERbin below D, EERbinD is used EERbin n between, interpolation
Note on O1: Author: No. of equivalent active mode hours for cooling=350 (Table A3 pg 57 14825-2016)
Note on G2: Author: =EERd(A)
Note on G3: Author: If Pc=DC , =EERd If not: Fixed EERbin=EERd(1-Cdc(1-CR) Variable/Staged 1) Increment compressoer capacity (step or level) until you reach Pc ±10%. Use measured Capacity & Pin. 2) If not within ±10%, get (Capacity within ±10% of Pc & Pin) for left & right pl conditions, interpol. Pin wrt measured Pc's, EER=Pc/Pin(interp) 3) If left or right step capacities are not within ±10% of Pc's, use the equation.
Note on N3: Author: No. of hours the unit is considered to work in Thermostat-off mode=221 (Table A3 pg 57 14825-2016) TO: the condition at which there is no cooling load and the cooling function is switched on but not operational
Note on O3: Author: Electricity consumption during TO
Note on G4: Author: If Pc=DC , =EERd If not: Fixed EERbin=EERd(1-Cdc(1-CR) Variable/Staged 1) Increment compressoer capacity (step or level) until you reach Pc ±10%. Use measured Capacity & Pin. 2) If not within ±10%, get (Capacity within ±10% of Pc & Pin) for left & right pl conditions, interpol. Pin wrt measured Pc's, EER=Pc/Pin(interp) 3) If left or right step capacities are not within ±10% of Pc's, use the equation.
Note on G5: Author: If Pc=DC , =EERd If not: Fixed EERbin=EERd(1-Cdc(1-CR) Variable/Staged 1) Increment compressoer capacity (step or level) until you reach Pc ±10%. Use measured Capacity & Pin. 2) If not within ±10%, get (Capacity within ±10% of Pc & Pin) for left & right pl conditions, interpol. Pin wrt measured Pc's, EER=Pc/Pin(interp) 3) If left or right step capacities are not within ±10% of Pc's, use the equation.
Note on N5: Author: No. of hours the unit is considered to work in stand-by mode=2142 (Table A3 pg 57 14825-2016)
Note on O5: Author: Electricity consumption during SB
Note on F6: Author: Degradation co-officient for cooling: One test at an outdoor dry bulb temperature of 20 °C with dry indoor coil One cyclic test at the same dry bulb temperature conditions, with dry indoor coil 1- Turn compressor on for 6 min, then off for 24 min (20% part-load) 2- If 6/24 does not satisfy uncertainty requirement in measuring cooling capacity, use interval representing up to 50% part-load (10/10) 3- Delivered cooling capacity is integrated over at least 4 on/off cycles (Pcycc), EERcyc=Pcycc/integrated Pin over that period 4- Qcontinuous=time integrated cooling capacity Pdc(integrated) that would have been delivered if the unit is always on 5- EERcontinuous=Qcontinuous/integrated continuous Pin 6- Cdc=(1-EERcyc/EERcontinuous) / (1-Pcycc/Qcontinuous)
Note on N7: Author: No. of hours the unit is considered to work in crankcase mode=7760 (Table A5 pg 57 14825-2016) =2672 for reversible AC CK: the condition where the unit has activated a heating device to avoid the refrigerant migrating to the compressor in order to limit the refrigerant concentration in oil at compressor start
Note on O7: Author: Electricity consumption during CK
Note on N9: Author: No. of hours the unit is considered to be off=5088 (Table A3 pg 57 14825-2016) =0 for reversible AC
Note on O9: Author: Electricity consumption when off